## DOASDXCOIL_wADPBFMethod_9.6 - C
EnergyPlus Output | [12 empty] | Manual Calculation
Date/Time | Environment:Site Outdoor Air Drybulb Temperature [C](Each Call) | VRF HEAT PUMP:VRF Heat Pump Total Cooling Rate [W](Each Call) | VRF HEAT PUMP:VRF Heat Pump Cooling Electricity Rate [W](Each Call) | VRF HEAT PUMP:VRF Heat Pump Cooling COP [](Each Call) | VRF HEAT PUMP:VRF Heat Pump Part Load Ratio [](Each Call) | VRF HEAT PUMP:VRF Heat Pump Runtime Fraction [](Each Call) | VRF HEAT PUMP:VRF Heat Pump Cycling Ratio [](Each Call) | SPACE1-1 TU DX CCOIL INLET NODE:System Node Wetbulb Temperature [C](Each Call) | SPACE2-1 TU DX CCOIL INLET NODE:System Node Wetbulb Temperature [C](Each Call) | SPACE3-1 TU DX CCOIL INLET NODE:System Node Wetbulb Temperature [C](Each Call) | SPACE4-1 TU DX CCOIL INLET NODE:System Node Wetbulb Temperature [C](Each Call) | SPACE5-1 TU DX CCOIL INLET NODE:System Node Wetbulb Temperature [C](Each Call) | Outdoor Air Temperature | Average Indoor Wetbulb Temperature | CoolCAPFT Coundary [C] | Cooling CAPFT | Full Load Cooling Capacity | Part Load Ratio | Cycling Ratio | Part Load Fraction | Run Time Fraction | EIRFT Boundary [C] | Cooling EIRFT | EIRfPLR | Cooling COP | Cooling Electricity Rate
07/16 00:15:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6012 | 18.5933 | 18.5753 | 18.6268 | 18.5346 | 26.7 | 18.5863 | 20.3376 | 1.0205 | 29181.3056 | 0 | 0 | 0 | 0 | 20.3376 | 0.84731 | 0.4729 | 0 | 0
07/16 00:30:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6123 | 18.6038 | 18.5857 | 18.6353 | 18.5459 | 26.7 | 18.5966 | 20.3331 | 1.0208 | 29189.4159 | 0 | 0 | 0 | 0 | 20.3331 | 0.84746 | 0.4729 | 0 | 0
07/16 00:45:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6204 | 18.6109 | 18.5928 | 18.6405 | 18.5552 | 26.7 | 18.6039 | 20.3299 | 1.021 | 29195.1762 | 0 | 0 | 0 | 0 | 20.3299 | 0.84756 | 0.4729 | 0 | 0
07/16 01:00:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6258 | 18.6154 | 18.5971 | 18.6433 | 18.5625 | 26.7 | 18.6088 | 20.3278 | 1.0212 | 29199.004 | 0 | 0 | 0 | 0 | 20.3278 | 0.84763 | 0.4729 | 0 | 0
07/16 01:15:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6265 | 18.615 | 18.5966 | 18.6414 | 18.5653 | 26.7 | 18.609 | 20.3278 | 1.0212 | 29199.1323 | 0 | 0 | 0 | 0 | 20.3278 | 0.84763 | 0.4729 | 0 | 0
07/16 01:30:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.626 | 18.6135 | 18.5949 | 18.6386 | 18.5663 | 26.7 | 18.6078 | 20.3282 | 1.0211 | 29198.241 | 0 | 0 | 0 | 0 | 20.3282 | 0.84761 | 0.4729 | 0 | 0
07/16 01:45:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6243 | 18.6109 | 18.5923 | 18.6348 | 18.5657 | 26.7 | 18.6056 | 20.3292 | 1.0211 | 29196.4724 | 0 | 0 | 0 | 0 | 20.3292 | 0.84758 | 0.4729 | 0 | 0
07/16 02:00:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6213 | 18.6074 | 18.5885 | 18.6295 | 18.5633 | 26.7 | 18.602 | 20.3308 | 1.021 | 29193.6757 | 0 | 0 | 0 | 0 | 20.3308 | 0.84753 | 0.4729 | 0 | 0
07/16 02:15:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6195 | 18.6051 | 18.586 | 18.6255 | 18.5619 | 26.7 | 18.5996 | 20.3318 | 1.0209 | 29191.7714 | 0 | 0 | 0 | 0 | 20.3318 | 0.8475 | 0.4729 | 0 | 0
07/16 02:30:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6211 | 18.606 | 18.5868 | 18.625 | 18.5638 | 26.7 | 18.6005 | 20.3314 | 1.0209 | 29192.5123 | 0 | 0 | 0 | 0 | 20.3314 | 0.84751 | 0.4729 | 0 | 0
07/16 02:45:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6291 | 18.6125 | 18.5938 | 18.6312 | 18.572 | 26.7 | 18.6077 | 20.3283 | 1.0211 | 29198.1574 | 0 | 0 | 0 | 0 | 20.3283 | 0.84761 | 0.4729 | 0 | 0
07/16 03:00:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6441 | 18.6258 | 18.6077 | 18.6445 | 18.5873 | 26.7 | 18.6219 | 20.3222 | 1.0215 | 29209.2704 | 0 | 0 | 0 | 0 | 20.3222 | 0.84781 | 0.4729 | 0 | 0
07/16 03:15:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6633 | 18.6432 | 18.6258 | 18.6617 | 18.6067 | 26.7 | 18.6402 | 20.3142 | 1.022 | 29223.6282 | 0 | 0 | 0 | 0 | 20.3142 | 0.84807 | 0.4729 | 0 | 0
07/16 03:30:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6822 | 18.6607 | 18.644 | 18.6789 | 18.6261 | 26.7 | 18.6584 | 20.3063 | 1.0225 | 29237.9336 | 0 | 0 | 0 | 0 | 20.3063 | 0.84832 | 0.4729 | 0 | 0
07/16 03:45:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6972 | 18.6744 | 18.6582 | 18.6921 | 18.6409 | 26.7 | 18.6726 | 20.3002 | 1.0229 | 29249.1342 | 0 | 0 | 0 | 0 | 20.3002 | 0.84852 | 0.4729 | 0 | 0
07/16 04:00:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7072 | 18.6835 | 18.6679 | 18.7008 | 18.6503 | 26.7 | 18.682 | 20.2961 | 1.0232 | 29256.5159 | 0 | 0 | 0 | 0 | 20.2961 | 0.84864 | 0.4729 | 0 | 0
07/16 04:15:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7178 | 18.6937 | 18.6786 | 18.7107 | 18.6601 | 26.7 | 18.6922 | 20.2917 | 1.0234 | 29264.553 | 0 | 0 | 0 | 0 | 20.2917 | 0.84878 | 0.4729 | 0 | 0
07/16 04:30:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7264 | 18.7023 | 18.6874 | 18.719 | 18.6682 | 26.7 | 18.7006 | 20.288 | 1.0237 | 29271.2358 | 0 | 0 | 0 | 0 | 20.288 | 0.8489 | 0.4729 | 0 | 0
07/16 04:45:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7347 | 18.7107 | 18.6956 | 18.7271 | 18.6764 | 26.7 | 18.7089 | 20.2844 | 1.0239 | 29277.7403 | 0 | 0 | 0 | 0 | 20.2844 | 0.84901 | 0.4729 | 0 | 0
07/16 05:00:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7433 | 18.7191 | 18.704 | 18.7353 | 18.6851 | 26.7 | 18.7173 | 20.2807 | 1.0241 | 29284.405 | 0 | 0 | 0 | 0 | 20.2807 | 0.84912 | 0.4729 | 0 | 0
07/16 05:15:00 | 26.825 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7495 | 18.7248 | 18.7098 | 18.741 | 18.6915 | 26.825 | 18.7233 | 20.2782 | 1.0235 | 29267.2265 | 0 | 0 | 0 | 0 | 20.2782 | 0.8519 | 0.4729 | 0 | 0
07/16 05:30:00 | 26.95 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7585 | 18.7327 | 18.718 | 18.7489 | 18.6993 | 26.95 | 18.7315 | 20.2746 | 1.023 | 29251.7399 | 0 | 0 | 0 | 0 | 20.2746 | 0.85471 | 0.4729 | 0 | 0
07/16 05:45:00 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7709 | 18.744 | 18.7298 | 18.7602 | 18.7089 | 27.075 | 18.7427 | 20.2697 | 1.0225 | 29238.7101 | 0 | 0 | 0 | 0 | 20.2697 | 0.85756 | 0.4729 | 0 | 0
07/16 06:00:00 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7899 | 18.7844 | 18.7824 | 18.7795 | 18.7205 | 27.2 | 18.7713 | 20.2573 | 1.0226 | 29239.3239 | 0 | 0 | 0 | 0 | 20.2573 | 0.86063 | 0.4729 | 0 | 0
07/16 06:07:30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18.8194 | 18.8615 | 18.8829 | 18.8114 | 18.7377 | 27.2 | 18.8226 | 20.235 | 1.024 | 29279.7355 | 0 | 0 | 0 | 0 | 20.235 | 0.86127 | 0.4729 | 0 | 0
07/16 06:15:00 | 27.475 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8262 | 18.89 | 18.9169 | 18.8188 | 18.7394 | 27.475 | 18.8383 | 20.2282 | 1.0227 | 29243.7541 | 0 | 0 | 0 | 0 | 20.2282 | 0.86742 | 0.4729 | 0 | 0
07/16 06:22:30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18.8397 | 18.9273 | 18.9628 | 18.8332 | 18.7469 | 27.475 | 18.862 | 20.2179 | 1.0234 | 29262.451 | 0 | 0 | 0 | 0 | 20.2179 | 0.8677 | 0.4729 | 0 | 0
07/16 06:30:00 | 27.75 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8752 | 19.0381 | 19.0968 | 18.8724 | 18.7634 | 27.75 | 18.9292 | 20.1885 | 1.0235 | 29267.0358 | 0 | 0 | 0 | 0 | 20.1885 | 0.87444 | 0.4729 | 0 | 0
07/16 06:37:30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18.8899 | 19.0749 | 19.1391 | 18.8884 | 18.7722 | 27.75 | 18.9529 | 20.1782 | 1.0242 | 29285.8004 | 0 | 0 | 0 | 0 | 20.1782 | 0.8747 | 0.4729 | 0 | 0
07/16 06:45:00 | 28.025 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9292 | 19.1866 | 19.2643 | 18.9329 | 18.7922 | 28.025 | 19.021 | 20.1483 | 1.0244 | 29291.0982 | 0 | 0 | 0 | 0 | 20.1483 | 0.8814 | 0.4729 | 0 | 0
07/16 06:52:30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18.9451 | 19.2249 | 19.3054 | 18.9508 | 18.8021 | 28.025 | 19.0457 | 20.1375 | 1.0251 | 29310.6045 | 0 | 0 | 0 | 0 | 20.1375 | 0.88165 | 0.4729 | 0 | 0
07/16 07:00:00 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9887 | 19.3458 | 19.4318 | 19.0017 | 18.826 | 28.3 | 19.1188 | 20.1053 | 1.0254 | 29319.8036 | 0 | 0 | 0 | 0 | 20.1053 | 0.88834 | 0.4729 | 0 | 0
07/16 07:03:45 |  | 7521.9075 | 4550.6216 | 1.6529 | 0.25465 | 1 | 1 | 19.0035 | 19.3853 | 19.4722 | 19.019 | 18.8347 | 28.3 | 19.1429 | 20.0946 | 1.026 | 29338.9576 | 0.25638 | 1 | 1 | 1 | 20.0946 | 0.88857 | 0.47486 | 6.5246 | 1152.8527
07/16 07:07:30 |  | 9.7993 | 7.0508 | 1.3898 | 0.25 | 0.0015794 | 0.0013428 | 18.9667 | 19.0007 | 18.9061 | 18.9877 | 18.8313 | 28.3 | 18.9385 | 20.1845 | 1.0204 | 29177.3746 | 0.25 | 0.0013434 | 0.8502 | 0.0015801 | 20.1845 | 0.88652 | 0.47291 | 6.5667 | 1.7552
07/16 07:11:15 |  | 183.0179 | 131.053 | 1.3965 | 0.25 | 0.029418 | 0.025116 | 18.9616 | 18.8685 | 18.6659 | 18.987 | 18.8338 | 28.3 | 18.8634 | 20.2172 | 1.0183 | 29118.3755 | 0.25 | 0.025141 | 0.85377 | 0.029447 | 20.2172 | 0.88569 | 0.47291 | 6.5728 | 32.6138
07/16 07:15:00 | 28.45 | 1782.8901 | 1226.7396 | 1.4534 | 0.25 | 0.277 | 0.24566 | 18.9661 | 18.9146 | 18.7077 | 18.987 | 18.8353 | 28.45 | 18.8821 | 20.2091 | 1.0179 | 29106.6874 | 0.25 | 0.24501 | 0.88675 | 0.27631 | 20.2091 | 0.88918 | 0.47291 | 6.547 | 307.1017
07/16 07:30:00 | 28.6 | 991.936 | 698.1456 | 1.4208 | 0.25 | 0.15704 | 0.1367 | 18.966 | 18.9155 | 18.7147 | 18.9868 | 18.8365 | 28.6 | 18.8839 | 20.2083 | 1.0171 | 29081.6616 | 0.25 | 0.13643 | 0.87047 | 0.15674 | 20.2083 | 0.89249 | 0.47291 | 6.5227 | 174.7054
07/16 07:45:00 | 28.75 | 2591.0388 | 1761.6174 | 1.4708 | 0.25 | 0.3962 | 0.35805 | 18.96 | 18.893 | 18.6334 | 18.9813 | 18.8354 | 28.75 | 18.8606 | 20.2184 | 1.0155 | 29037.0654 | 0.25 | 0.35693 | 0.90354 | 0.39503 | 20.2184 | 0.89554 | 0.47291 | 6.5005 | 441.1432
07/16 08:00:00 | 28.9 | 2720.0221 | 1850.3572 | 1.47 | 0.25 | 0.41514 | 0.3763 | 18.9571 | 18.8863 | 18.6065 | 18.9788 | 18.8452 | 28.9 | 18.8548 | 20.221 | 1.0144 | 29006.1305 | 0.25 | 0.3751 | 0.90626 | 0.41389 | 20.221 | 0.89878 | 0.47291 | 6.4771 | 463.3826
07/16 08:15:00 | 29.025 | 2359.3376 | 1622.6696 | 1.454 | 0.25 | 0.36359 | 0.32688 | 18.9564 | 18.887 | 18.6101 | 18.9784 | 18.8609 | 29.025 | 18.8586 | 20.2193 | 1.0137 | 28987.085 | 0.25 | 0.32557 | 0.89884 | 0.36221 | 20.2193 | 0.90158 | 0.47291 | 6.4569 | 406.5213
07/16 08:30:00 | 29.15 | 3102.127 | 2102.0847 | 1.4757 | 0.25 | 0.47098 | 0.43077 | 18.8149 | 18.789 | 18.5512 | 18.8362 | 18.6399 | 29.15 | 18.7262 | 20.2769 | 1.0094 | 28862.4351 | 0.25 | 0.42992 | 0.91449 | 0.47012 | 20.2769 | 0.90286 | 0.47291 | 6.4478 | 526.1052
07/16 08:45:00 | 29.275 | 3646.2807 | 2443.1994 | 1.4924 | 0.25 | 0.54883 | 0.50836 | 18.607 | 18.6453 | 18.4473 | 18.6333 | 18.3614 | 29.275 | 18.5388 | 20.3582 | 1.0036 | 28696.3841 | 0.25 | 0.50826 | 0.92624 | 0.54873 | 20.3582 | 0.90335 | 0.47291 | 6.4443 | 610.8757
07/16 09:00:00 | 29.4 | 4094.6612 | 2719.0215 | 1.5059 | 0.25 | 0.61227 | 0.57306 | 18.4273 | 18.5187 | 18.3505 | 18.462 | 18.1629 | 29.4 | 18.3843 | 20.4252 | 0.9987 | 28556.8185 | 0.25 | 0.57355 | 0.93603 | 0.61274 | 20.4252 | 0.90409 | 0.47291 | 6.439 | 679.3715
07/16 09:07:30 |  | 5986.9122 | 3807.3077 | 1.5725 | 0.25 | 0.86053 | 0.83986 | 18.3059 | 18.418 | 18.28 | 18.3461 | 18.0594 | 29.4 | 18.2819 | 20.4697 | 0.99598 | 28479.2399 | 0.25 | 0.84088 | 0.97613 | 0.86144 | 20.4697 | 0.90263 | 0.47291 | 6.4494 | 950.9849
07/16 09:15:00 | 29.4 | 7050.1851 | 4377.9745 | 1.6104 | 0.25 | 0.99194 | 0.99053 | 18.3089 | 18.3475 | 18.2357 | 18.3427 | 18.1776 | 29.4 | 18.2825 | 20.4694 | 0.996 | 28479.6927 | 0.25 | 0.99021 | 0.99853 | 0.99166 | 20.4694 | 0.90264 | 0.47291 | 6.4494 | 1094.7693
07/16 09:22:30 |  | 7073.412 | 4387.5459 | 1.6122 | 0.25 | 0.9954 | 0.99459 | 18.2862 | 18.2884 | 18.1959 | 18.3185 | 18.1687 | 29.4 | 18.2516 | 20.4829 | 0.99518 | 28456.328 | 0.25 | 0.99428 | 0.99914 | 0.99514 | 20.4829 | 0.90219 | 0.47291 | 6.4526 | 1097.1507
07/16 09:30:00 | 29.4 | 7012.9647 | 4345.9434 | 1.6137 | 0.25 | 0.99053 | 0.98888 | 18.2224 | 18.1232 | 18.0841 | 18.2528 | 18.1284 | 29.4 | 18.1622 | 20.5219 | 0.99283 | 28389.0117 | 0.25 | 0.98812 | 0.99822 | 0.98989 | 20.5219 | 0.90084 | 0.47291 | 6.4623 | 1087.151
07/16 09:37:30 |  | 7298.8234 | 4404.5442 | 1.6571 | 0.25744 | 1 | 1 | 18.2082 | 18.0855 | 18.0594 | 18.238 | 18.1198 | 29.4 | 18.1422 | 20.5306 | 0.9923 | 28373.9926 | 0.25724 | 1 | 1 | 1 | 20.5306 | 0.90053 | 0.47512 | 6.4343 | 1134.3556
07/16 09:45:00 | 29.4 | 7241.008 | 4387.7254 | 1.6503 | 0.25583 | 1 | 1 | 18.1637 | 17.9861 | 17.9973 | 18.1921 | 18.0891 | 29.4 | 18.0857 | 20.5554 | 0.99082 | 28331.6164 | 0.25558 | 1 | 1 | 1 | 20.5554 | 0.89963 | 0.47461 | 6.4477 | 1123.0382
07/16 09:52:30 |  | 7338.3994 | 4396.1177 | 1.6693 | 0.25933 | 1 | 1 | 18.1534 | 17.9653 | 17.9872 | 18.1812 | 18.0831 | 29.4 | 18.074 | 20.5605 | 0.99052 | 28322.9165 | 0.2591 | 1 | 1 | 1 | 20.5605 | 0.89945 | 0.47571 | 6.4341 | 1140.5426
07/16 10:00:00 | 29.4 | 7315.2589 | 4387.8532 | 1.6672 | 0.25874 | 1 | 1 | 18.1193 | 17.9131 | 17.9621 | 18.1452 | 18.0597 | 29.4 | 18.0399 | 20.5755 | 0.98962 | 28297.3761 | 0.25851 | 1 | 1 | 1 | 20.5755 | 0.8989 | 0.47552 | 6.4406 | 1135.8091
07/16 10:07:30 |  | 7513.7169 | 4434.5356 | 1.6944 | 0.26628 | 1 | 1 | 18.1069 | 17.8999 | 17.9561 | 18.132 | 18.0506 | 29.4 | 18.0291 | 20.5802 | 0.98934 | 28289.3357 | 0.2656 | 1 | 1 | 1 | 20.5802 | 0.89872 | 0.47779 | 6.4112 | 1171.9594
07/16 10:15:00 | 29.7 | 7512.823 | 4432.6136 | 1.6949 | 0.26632 | 1 | 1 | 18.087 | 17.8832 | 17.9577 | 18.11 | 18.0395 | 29.7 | 18.0155 | 20.5862 | 0.9872 | 28228.0336 | 0.26615 | 1 | 1 | 1 | 20.5862 | 0.90534 | 0.47797 | 6.362 | 1180.8872
07/16 10:22:30 |  | 7541.2753 | 4462.8364 | 1.6898 | 0.26781 | 1 | 1 | 18.0813 | 17.8801 | 17.9591 | 18.1033 | 18.0367 | 29.7 | 18.0121 | 20.5877 | 0.98711 | 28225.5069 | 0.26718 | 1 | 1 | 1 | 20.5877 | 0.90528 | 0.47831 | 6.3579 | 1186.1248
07/16 10:30:00 | 30 | 7551.0726 | 4465.4635 | 1.691 | 0.2681 | 1 | 1 | 18.0796 | 17.8922 | 17.9769 | 18.0984 | 18.0432 | 30 | 18.0181 | 20.5851 | 0.98548 | 28178.8366 | 0.26797 | 1 | 1 | 1 | 20.5851 | 0.91224 | 0.47857 | 6.306 | 1197.4493
07/16 10:37:30 |  | 7706.6246 | 4510.8337 | 1.7085 | 0.27408 | 1 | 1 | 18.0789 | 17.8968 | 17.9821 | 18.0965 | 18.0453 | 30 | 18.0199 | 20.5843 | 0.98552 | 28180.2016 | 0.27348 | 1 | 1 | 1 | 20.5843 | 0.91227 | 0.48041 | 6.2816 | 1226.8503
07/16 10:45:00 | 30.3 | 7716.3796 | 4515.4147 | 1.7089 | 0.27428 | 1 | 1 | 18.0898 | 17.9239 | 18.0079 | 18.104 | 18.0641 | 30.3 | 18.038 | 20.5764 | 0.9842 | 28142.4488 | 0.27419 | 1 | 1 | 1 | 20.5764 | 0.91945 | 0.48065 | 6.2295 | 1238.6842
07/16 10:52:30 |  | 7845.0931 | 4558.8361 | 1.7209 | 0.27931 | 1 | 1 | 18.0926 | 17.9301 | 18.015 | 18.1057 | 18.0694 | 30.3 | 18.0426 | 20.5743 | 0.98432 | 28145.8629 | 0.27873 | 1 | 1 | 1 | 20.5743 | 0.91952 | 0.4822 | 6.2089 | 1263.5229
07/16 11:00:00 | 30.6 | 7857.8948 | 4564.9147 | 1.7214 | 0.27957 | 1 | 1 | 18.1128 | 17.9619 | 18.0461 | 18.1222 | 18.0967 | 30.6 | 18.0679 | 20.5632 | 0.98319 | 28113.4737 | 0.27951 | 1 | 1 | 1 | 20.5632 | 0.92682 | 0.48247 | 6.1566 | 1276.3418
07/16 11:07:30 |  | 7071.5395 | 4480.3878 | 1.5783 | 0.25153 | 1 | 1 | 18.1208 | 17.9723 | 18.0572 | 18.129 | 18.1068 | 30.6 | 18.0772 | 20.5591 | 0.98343 | 28120.3565 | 0.25147 | 1 | 1 | 1 | 20.5591 | 0.92696 | 0.47335 | 6.2743 | 1127.0704
07/16 11:15:00 | 30.6 | 7074.3194 | 4480.9176 | 1.5788 | 0.25162 | 1 | 1 | 18.1157 | 17.9816 | 18.0619 | 18.1214 | 18.1062 | 30.6 | 18.0774 | 20.559 | 0.98344 | 28120.4796 | 0.25157 | 1 | 1 | 1 | 20.559 | 0.92696 | 0.47338 | 6.2739 | 1127.5871
07/16 11:22:30 |  | 6916.9084 | 4414.8212 | 1.5667 | 0.25 | 0.98663 | 0.9843 | 18.1031 | 17.9776 | 18.0531 | 18.1089 | 18.0935 | 30.6 | 18.0672 | 20.5635 | 0.98317 | 28112.9718 | 0.25 | 0.98416 | 0.99762 | 0.9865 | 20.5635 | 0.92681 | 0.47291 | 6.2812 | 1103.8311
07/16 11:30:00 | 30.6 | 6919.702 | 4413.4861 | 1.5679 | 0.25 | 0.98766 | 0.98552 | 18.0631 | 17.9633 | 18.0246 | 18.0709 | 18.0511 | 30.6 | 18.0346 | 20.5778 | 0.98233 | 28088.8166 | 0.25 | 0.9854 | 0.99781 | 0.98757 | 20.5778 | 0.9263 | 0.47291 | 6.2846 | 1103.4715
07/16 11:37:30 |  | 6778.7906 | 4335.8249 | 1.5634 | 0.25 | 0.97069 | 0.96569 | 18.05 | 17.9577 | 18.0148 | 18.0585 | 18.037 | 30.6 | 18.0236 | 20.5827 | 0.98205 | 28080.7047 | 0.25 | 0.96562 | 0.99484 | 0.97062 | 20.5827 | 0.92613 | 0.47291 | 6.2858 | 1084.026
07/16 11:45:00 | 30.6 | 6779.0287 | 4333.0585 | 1.5645 | 0.25 | 0.97142 | 0.96654 | 18.0116 | 17.9391 | 17.9854 | 18.0221 | 17.9955 | 30.6 | 17.9908 | 20.5971 | 0.9812 | 28056.4444 | 0.25 | 0.96648 | 0.99497 | 0.97137 | 20.5971 | 0.92562 | 0.47291 | 6.2893 | 1083.3181
07/16 11:52:30 |  | 6758.6021 | 4320.9956 | 1.5641 | 0.25 | 0.96913 | 0.96388 | 17.9991 | 17.9322 | 17.9754 | 18.01 | 17.9825 | 30.6 | 17.9799 | 20.602 | 0.98092 | 28048.4057 | 0.25 | 0.96385 | 0.99458 | 0.9691 | 20.602 | 0.92544 | 0.47291 | 6.2904 | 1080.2814
07/16 12:00:00 | 30.6 | 6760.4248 | 4318.9977 | 1.5653 | 0.25 | 0.97007 | 0.96498 | 17.9618 | 17.9101 | 17.9446 | 17.9739 | 17.9433 | 30.6 | 17.9467 | 20.6166 | 0.98006 | 28024.0124 | 0.25 | 0.96495 | 0.99474 | 0.97005 | 20.6166 | 0.92491 | 0.47291 | 6.2941 | 1079.7747
07/16 12:07:30 |  | 5244.3675 | 3473.2223 | 1.5099 | 0.25 | 0.77863 | 0.74936 | 17.9494 | 17.902 | 17.9339 | 17.9617 | 17.9307 | 30.6 | 17.9355 | 20.6215 | 0.97977 | 28015.7679 | 0.25 | 0.74877 | 0.96232 | 0.7781 | 20.6215 | 0.92473 | 0.47291 | 6.2953 | 865.6852
07/16 12:15:00 | 30.725 | 5485.9682 | 3608.5548 | 1.5203 | 0.25 | 0.81144 | 0.78531 | 17.8757 | 17.8417 | 17.8665 | 17.8896 | 17.8527 | 30.725 | 17.8652 | 20.6527 | 0.97723 | 27942.9625 | 0.25 | 0.78531 | 0.9678 | 0.81144 | 20.6527 | 0.92648 | 0.47291 | 6.2834 | 902.1361
07/16 12:22:30 |  | 5424.9532 | 3581.932 | 1.5145 | 0.25 | 0.80458 | 0.77776 | 17.8448 | 17.8157 | 17.8378 | 17.8597 | 17.8194 | 30.725 | 17.8355 | 20.666 | 0.97647 | 27921.1917 | 0.25 | 0.77718 | 0.96658 | 0.80405 | 20.666 | 0.92598 | 0.47291 | 6.2868 | 892.7485
07/16 12:30:00 | 30.85 | 5430.2444 | 3579.6339 | 1.517 | 0.25 | 0.80656 | 0.77994 | 17.7709 | 17.7558 | 17.77 | 17.7901 | 17.7377 | 30.85 | 17.7649 | 20.6975 | 0.97393 | 27848.5884 | 0.25 | 0.77997 | 0.967 | 0.80659 | 20.6975 | 0.92769 | 0.47291 | 6.2752 | 894.8812
07/16 12:37:30 |  | 5446.644 | 3598.8081 | 1.5135 | 0.25 | 0.80955 | 0.78322 | 17.7538 | 17.7414 | 17.7539 | 17.7733 | 17.7195 | 30.85 | 17.7484 | 20.7049 | 0.97351 | 27836.5779 | 0.25 | 0.78266 | 0.9674 | 0.80904 | 20.7049 | 0.9274 | 0.47291 | 6.2772 | 896.933
07/16 12:45:00 | 30.975 | 5450.2361 | 3597.8756 | 1.5148 | 0.25 | 0.81073 | 0.78452 | 17.7135 | 17.708 | 17.7163 | 17.734 | 17.6781 | 30.975 | 17.71 | 20.7222 | 0.97179 | 27787.6128 | 0.25 | 0.78456 | 0.96768 | 0.81076 | 20.7222 | 0.92965 | 0.47291 | 6.262 | 899.4378
07/16 12:52:30 |  | 5533.1727 | 3656.2638 | 1.5133 | 0.25 | 0.82227 | 0.79726 | 17.7039 | 17.6996 | 17.707 | 17.7239 | 17.6694 | 30.975 | 17.7007 | 20.7264 | 0.97156 | 27780.923 | 0.25 | 0.79669 | 0.9695 | 0.82175 | 20.7264 | 0.92949 | 0.47291 | 6.2631 | 911.252
07/16 13:00:00 | 31.1 | 5534.549 | 3655.4284 | 1.5141 | 0.25 | 0.82283 | 0.79788 | 17.6827 | 17.6814 | 17.6865 | 17.7016 | 17.6513 | 31.1 | 17.6807 | 20.7354 | 0.97032 | 27745.3691 | 0.25 | 0.79791 | 0.96969 | 0.82285 | 20.7354 | 0.93206 | 0.47291 | 6.2458 | 913.8306
07/16 13:07:30 |  | 6928.9017 | 4437.5037 | 1.5614 | 0.25 | 0.99924 | 0.99911 | 17.6757 | 17.6749 | 17.6795 | 17.6939 | 17.6459 | 31.1 | 17.674 | 20.7385 | 0.97015 | 27740.5302 | 0.25 | 0.9991 | 0.99987 | 0.99924 | 20.7385 | 0.93195 | 0.47291 | 6.2466 | 1109.3851
07/16 13:15:00 | 31.1 | 6925.9723 | 4439.3939 | 1.5601 | 0.25 | 0.99812 | 0.99779 | 17.7097 | 17.709 | 17.7123 | 17.7246 | 17.6869 | 31.1 | 17.7085 | 20.7229 | 0.97102 | 27765.5003 | 0.25 | 0.99778 | 0.99967 | 0.99811 | 20.7229 | 0.93255 | 0.47291 | 6.2425 | 1109.8576
07/16 13:22:30 |  | 7114.8842 | 4470.4002 | 1.5916 | 0.25608 | 1 | 1 | 17.7357 | 17.7339 | 17.7371 | 17.7479 | 17.717 | 31.1 | 17.7343 | 20.7113 | 0.97168 | 27784.2294 | 0.25608 | 1 | 1 | 1 | 20.7113 | 0.933 | 0.47476 | 6.2151 | 1144.7755
07/16 13:30:00 | 31.1 | 6941.1943 | 4457.9998 | 1.557 | 0.25 | 0.99768 | 0.99727 | 17.8144 | 17.8075 | 17.812 | 17.8167 | 17.8102 | 31.1 | 17.8122 | 20.6764 | 0.97365 | 27840.7744 | 0.25 | 0.99727 | 0.99959 | 0.99768 | 20.6764 | 0.93433 | 0.47291 | 6.2307 | 1114.4958
07/16 13:37:30 |  | 7133.3678 | 4488.9864 | 1.5891 | 0.25612 | 1 | 1 | 17.8293 | 17.8212 | 17.8261 | 17.829 | 17.8287 | 31.1 | 17.8269 | 20.6698 | 0.97403 | 27851.4793 | 0.25612 | 1 | 1 | 1 | 20.6698 | 0.93457 | 0.47478 | 6.2045 | 1149.7129
07/16 13:45:00 | 31.1 | 7134.0384 | 4496.1764 | 1.5867 | 0.25587 | 1 | 1 | 17.8697 | 17.859 | 17.865 | 17.8632 | 17.8773 | 31.1 | 17.8668 | 20.652 | 0.97505 | 27880.6356 | 0.25588 | 1 | 1 | 1 | 20.652 | 0.93523 | 0.4747 | 6.2011 | 1150.4488
07/16 14:00:00 | 31.1 | 7393.197 | 4527.2178 | 1.6331 | 0.26505 | 1 | 1 | 17.8873 | 17.8765 | 17.8821 | 17.879 | 17.897 | 31.1 | 17.8844 | 20.6442 | 0.9755 | 27893.4409 | 0.26505 | 1 | 1 | 1 | 20.6442 | 0.93552 | 0.47761 | 6.1614 | 1199.9221
07/16 14:15:00 | 31.1 | 8095.6035 | 4613.3798 | 1.7548 | 0.29006 | 1 | 1 | 17.9097 | 17.8988 | 17.9038 | 17.8993 | 17.9218 | 31.1 | 17.9067 | 20.6343 | 0.97607 | 27909.7514 | 0.29006 | 1 | 1 | 1 | 20.6343 | 0.93588 | 0.48623 | 6.0499 | 1338.1405
07/16 14:30:00 | 31.1 | 8448.2835 | 4669.4051 | 1.8093 | 0.30218 | 1 | 1 | 17.9758 | 17.9625 | 17.9683 | 17.9572 | 17.9946 | 31.1 | 17.9717 | 20.6056 | 0.97773 | 27957.3642 | 0.30218 | 1 | 1 | 1 | 20.6056 | 0.93691 | 0.49075 | 5.9875 | 1410.9763
07/16 14:45:00 | 31.1 | 8669.0712 | 4711.6977 | 1.8399 | 0.30945 | 1 | 1 | 18.0543 | 18.0369 | 18.0442 | 18.0238 | 18.083 | 31.1 | 18.0484 | 20.5717 | 0.9797 | 28013.7864 | 0.30946 | 1 | 1 | 1 | 20.5717 | 0.93808 | 0.49357 | 5.9459 | 1458.0031
07/16 15:00:00 | 31.1 | 8808.6069 | 4742.7451 | 1.8573 | 0.31383 | 1 | 1 | 18.1223 | 18.1093 | 18.1177 | 18.0878 | 18.1677 | 31.1 | 18.121 | 20.5399 | 0.98158 | 28067.3056 | 0.31384 | 1 | 1 | 1 | 20.5399 | 0.93916 | 0.49531 | 5.9182 | 1488.3902
07/16 15:15:00 | 30.975 | 8145.685 | 4654.9127 | 1.7499 | 0.28953 | 1 | 1 | 18.1699 | 18.1742 | 18.1836 | 18.1465 | 18.2413 | 30.975 | 18.1831 | 20.5128 | 0.98393 | 28134.7189 | 0.28952 | 1 | 1 | 1 | 20.5128 | 0.93716 | 0.48603 | 6.044 | 1347.7292
07/16 15:30:00 | 30.85 | 7822.7908 | 4609.972 | 1.6969 | 0.2776 | 1 | 1 | 18.1988 | 18.2085 | 18.2183 | 18.1776 | 18.2755 | 30.85 | 18.2158 | 20.4985 | 0.98553 | 28180.4371 | 0.2776 | 1 | 1 | 1 | 20.4985 | 0.93475 | 0.48181 | 6.1127 | 1279.7548
07/16 15:45:00 | 30.725 | 7733.9695 | 4587.805 | 1.6858 | 0.27426 | 1 | 1 | 18.199 | 18.2068 | 18.2157 | 18.1788 | 18.2634 | 30.725 | 18.2127 | 20.4998 | 0.9862 | 28199.6438 | 0.27426 | 1 | 1 | 1 | 20.4998 | 0.93183 | 0.48067 | 6.1464 | 1258.2859
07/16 16:00:00 | 30.6 | 7747.3828 | 4572.2185 | 1.6944 | 0.27478 | 1 | 1 | 18.1674 | 18.1745 | 18.1813 | 18.1547 | 18.213 | 30.6 | 18.1782 | 20.5149 | 0.98605 | 28195.3166 | 0.27478 | 1 | 1 | 1 | 20.5149 | 0.92846 | 0.48085 | 6.1665 | 1256.3706
07/16 16:15:00 | 30.3 | 6947.4049 | 4405.1404 | 1.5771 | 0.25 | 0.98743 | 0.98524 | 18.1145 | 18.1233 | 18.1275 | 18.1161 | 18.1396 | 30.3 | 18.1242 | 20.5385 | 0.98645 | 28206.5229 | 0.25 | 0.98522 | 0.99778 | 0.98741 | 20.5385 | 0.92077 | 0.47291 | 6.3223 | 1101.3062
07/16 16:30:00 | 30 | 6893.0731 | 4339.4234 | 1.5885 | 0.25 | 0.98051 | 0.97715 | 18.06 | 18.0713 | 18.0731 | 18.076 | 18.0674 | 30 | 18.0695 | 20.5625 | 0.98682 | 28217.1011 | 0.25 | 0.97715 | 0.99657 | 0.98051 | 20.5625 | 0.91306 | 0.47291 | 6.3758 | 1084.856
07/16 16:45:00 | 29.7 | 6735.931 | 4219.7787 | 1.5963 | 0.25 | 0.96088 | 0.95429 | 18.0135 | 18.0267 | 18.0266 | 18.0408 | 18.0083 | 29.7 | 18.0232 | 20.5829 | 0.9874 | 28233.7443 | 0.25 | 0.95431 | 0.99315 | 0.96089 | 20.5829 | 0.90546 | 0.47291 | 6.4293 | 1054.929
07/16 17:00:00 | 29.4 | 6470.6197 | 4043.4907 | 1.6003 | 0.25 | 0.92767 | 0.91598 | 17.9744 | 17.9886 | 17.9872 | 18.0095 | 17.9616 | 29.4 | 17.9843 | 20.6 | 0.98817 | 28255.8755 | 0.25 | 0.916 | 0.9874 | 0.92769 | 20.6 | 0.89798 | 0.47291 | 6.4828 | 1010.852
07/16 17:15:00 | 29.275 | 6150.9217 | 3855.0005 | 1.5956 | 0.25 | 0.88817 | 0.87098 | 17.9348 | 17.949 | 17.9469 | 17.9743 | 17.9179 | 29.275 | 17.9446 | 20.6175 | 0.98788 | 28247.5943 | 0.25 | 0.871 | 0.98065 | 0.88819 | 20.6175 | 0.89446 | 0.47291 | 6.5083 | 963.7344
07/16 17:30:00 | 29.15 | 5847.0335 | 3674.8934 | 1.5911 | 0.25 | 0.84993 | 0.828 | 17.9048 | 17.9186 | 17.9161 | 17.9457 | 17.8866 | 29.15 | 17.9144 | 20.6309 | 0.98784 | 28246.3457 | 0.25 | 0.82801 | 0.9742 | 0.84993 | 20.6309 | 0.8911 | 0.47291 | 6.5329 | 918.7161
07/16 17:45:00 | 29.025 | 5539.3887 | 3492.5611 | 1.5861 | 0.25 | 0.81049 | 0.78426 | 17.8855 | 17.8982 | 17.8955 | 17.9246 | 17.8681 | 29.025 | 17.8944 | 20.6398 | 0.98806 | 28252.6958 | 0.25 | 0.78426 | 0.96764 | 0.81049 | 20.6398 | 0.88791 | 0.47291 | 6.5564 | 873.1397
07/16 18:00:00 | 28.9 | 5217.562 | 3301.8554 | 1.5802 | 0.25 | 0.76853 | 0.73837 | 17.875 | 17.8862 | 17.8837 | 17.9104 | 17.86 | 28.9 | 17.8831 | 20.6448 | 0.98851 | 28265.4694 | 0.25 | 0.73837 | 0.96075 | 0.76853 | 20.6448 | 0.88487 | 0.47291 | 6.5789 | 825.4686
07/16 18:15:00 | 28.75 | 1965.2415 | 1335.0863 | 1.472 | 0.25 | 0.31156 | 0.27781 | 17.8766 | 17.8858 | 17.8836 | 17.9068 | 17.8646 | 28.75 | 17.8835 | 20.6446 | 0.98941 | 28291.2146 | 0.25 | 0.27786 | 0.89168 | 0.31161 | 20.6446 | 0.88147 | 0.47291 | 6.6043 | 333.7201
07/16 18:30:00 | 28.6 | 1472.3857 | 1006.8797 | 1.4623 | 0.25 | 0.23637 | 0.2083 | 17.8095 | 17.818 | 17.8167 | 17.8456 | 17.7552 | 28.6 | 17.809 | 20.6778 | 0.98836 | 28261.1717 | 0.25 | 0.2084 | 0.88126 | 0.23648 | 20.6778 | 0.87672 | 0.47291 | 6.6401 | 251.6201
07/16 18:45:00 | 28.45 | 1155.7162 | 791.8135 | 1.4596 | 0.25 | 0.18721 | 0.16372 | 17.7142 | 17.7242 | 17.7227 | 17.7653 | 17.5929 | 28.45 | 17.7038 | 20.725 | 0.98651 | 28208.4317 | 0.25 | 0.16388 | 0.87458 | 0.18738 | 20.725 | 0.87133 | 0.47291 | 6.6811 | 197.7885
07/16 19:00:00 | 28.3 | 838.0958 | 575.3758 | 1.4566 | 0.25 | 0.13697 | 0.11887 | 17.6241 | 17.6353 | 17.6331 | 17.6894 | 17.4492 | 28.3 | 17.6062 | 20.7692 | 0.98487 | 28161.4745 | 0.25 | 0.11904 | 0.86786 | 0.13717 | 20.7692 | 0.866 | 0.47291 | 6.7222 | 143.659
07/16 19:07:30 |  | 124.1082 | 86.3603 | 1.4371 | 0.25 | 0.020651 | 0.017608 | 17.5485 | 17.5593 | 17.5568 | 17.622 | 17.3393 | 28.3 | 17.5252 | 20.8063 | 0.98278 | 28101.7225 | 0.25 | 0.017666 | 0.85265 | 0.020718 | 20.8063 | 0.86435 | 0.47291 | 6.735 | 21.6117
07/16 19:15:00 | 28.175 | 124.6118 | 86.5807 | 1.4393 | 0.25 | 0.020769 | 0.017708 | 17.4397 | 17.4484 | 17.4447 | 17.5589 | 17.2203 | 28.175 | 17.4224 | 20.8537 | 0.98087 | 28047.1573 | 0.25 | 0.017772 | 0.85267 | 0.020843 | 20.8537 | 0.85934 | 0.47291 | 6.7743 | 21.5732
07/16 19:22:30 |  | 11.6421 | 8.074 | 1.4419 | 0.25 | 0.0019473 | 0.0016557 | 17.3537 | 17.3615 | 17.3566 | 17.5016 | 17.1206 | 28.175 | 17.3388 | 20.8927 | 0.97874 | 27986.0693 | 0.25 | 0.001664 | 0.85025 | 0.001957 | 20.8927 | 0.85753 | 0.47291 | 6.7887 | 2.017
07/16 19:30:00 | 28.05 | 12.0197 | 8.2992 | 1.4483 | 0.25 | 0.0020196 | 0.0017172 | 17.1036 | 17.1072 | 17.1005 | 17.3269 | 16.8479 | 28.05 | 17.0972 | 21.0079 | 0.97333 | 27831.4757 | 0.25 | 0.0017275 | 0.85026 | 0.0020317 | 21.0079 | 0.84913 | 0.47291 | 6.8558 | 2.062
07/16 19:37:30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17.0456 | 17.0479 | 17.0411 | 17.2797 | 16.7908 | 28.05 | 17.041 | 21.0352 | 0.97191 | 27790.9749 | 0 | 0 | 0 | 0 | 21.0352 | 0.84778 | 0.4729 | 0 | 0
07/16 19:45:00 | 27.925 | 0 | 0 | 0 | 0 | 0 | 0 | 16.9563 | 16.9566 | 16.948 | 17.1928 | 16.7125 | 27.925 | 16.9533 | 21.0784 | 0.97043 | 27748.4413 | 0 | 0 | 0 | 0 | 21.0784 | 0.84275 | 0.4729 | 0 | 0
07/16 19:52:30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16.9669 | 16.9675 | 16.9578 | 17.1949 | 16.7282 | 27.925 | 16.963 | 21.0735 | 0.97067 | 27755.4589 | 0 | 0 | 0 | 0 | 21.0735 | 0.84299 | 0.4729 | 0 | 0
07/16 20:00:00 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 17.0434 | 17.0457 | 17.0316 | 17.2434 | 16.8213 | 27.8 | 17.0371 | 21.0371 | 0.97325 | 27829.226 | 0 | 0 | 0 | 0 | 21.0371 | 0.84193 | 0.4729 | 0 | 0
07/16 20:07:30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17.0833 | 17.0864 | 17.0709 | 17.2765 | 16.8659 | 27.8 | 17.0766 | 21.0179 | 0.97425 | 27857.7349 | 0 | 0 | 0 | 0 | 21.0179 | 0.84289 | 0.4729 | 0 | 0
07/16 20:15:00 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2339 | 17.2399 | 17.2197 | 17.4074 | 17.0299 | 27.8 | 17.2262 | 20.9459 | 0.97804 | 27966.1982 | 0 | 0 | 0 | 0 | 20.9459 | 0.84641 | 0.4729 | 0 | 0
07/16 20:22:30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17.288 | 17.2948 | 17.2734 | 17.4566 | 17.0873 | 27.8 | 17.28 | 20.9204 | 0.97941 | 28005.451 | 0 | 0 | 0 | 0 | 20.9204 | 0.84764 | 0.4729 | 0 | 0
07/16 20:30:00 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4693 | 17.4789 | 17.4537 | 17.6221 | 17.2788 | 27.8 | 17.4606 | 20.836 | 0.98404 | 28137.8089 | 0 | 0 | 0 | 0 | 20.836 | 0.85162 | 0.4729 | 0 | 0
07/16 20:37:30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17.5311 | 17.5413 | 17.5153 | 17.6794 | 17.3434 | 27.8 | 17.5221 | 20.8077 | 0.98563 | 28183.1812 | 0 | 0 | 0 | 0 | 20.8077 | 0.85292 | 0.4729 | 0 | 0
07/16 20:45:00 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7305 | 17.7427 | 17.714 | 17.8645 | 17.5512 | 27.8 | 17.7206 | 20.7175 | 0.99078 | 28330.4636 | 0 | 0 | 0 | 0 | 20.7175 | 0.85695 | 0.4729 | 0 | 0
07/16 21:00:00 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8608 | 17.8738 | 17.8441 | 17.9869 | 17.6864 | 27.8 | 17.8504 | 20.6593 | 0.99418 | 28427.5899 | 0 | 0 | 0 | 0 | 20.6593 | 0.85943 | 0.4729 | 0 | 0
07/16 21:07:30 |  | 285.9331 | 197.0769 | 1.4509 | 0.25 | 0.046553 | 0.039849 | 18.0654 | 18.0792 | 18.0484 | 18.1792 | 17.8978 | 27.8 | 18.054 | 20.5693 | 0.99955 | 28581.1371 | 0.25 | 0.040017 | 0.856 | 0.046749 | 20.5693 | 0.86309 | 0.47291 | 6.7449 | 49.5239
07/16 21:15:00 | 27.525 | 1508.7541 | 1008.5446 | 1.496 | 0.25 | 0.23887 | 0.21058 | 18.0868 | 18.109 | 18.0795 | 18.1288 | 17.9204 | 27.525 | 18.0649 | 20.5645 | 1.0015 | 28636.3835 | 0.25 | 0.21075 | 0.88161 | 0.23905 | 20.5645 | 0.85716 | 0.47291 | 6.7916 | 251.9823
07/16 21:22:30 |  | 1223.5679 | 817.1904 | 1.4973 | 0.25 | 0.19487 | 0.17063 | 18.1023 | 18.1241 | 18.0967 | 18.1442 | 17.9921 | 27.525 | 18.0919 | 20.5527 | 1.0022 | 28656.9145 | 0.25 | 0.17079 | 0.87562 | 0.19505 | 20.5527 | 0.85762 | 0.47291 | 6.7879 | 205.8631
07/16 21:30:00 | 27.25 | 1134.1358 | 760.1647 | 1.492 | 0.25 | 0.18069 | 0.15787 | 18.1322 | 18.1524 | 18.128 | 18.1723 | 18.1074 | 27.25 | 18.1385 | 20.5323 | 1.0051 | 28739.5373 | 0.25 | 0.15785 | 0.87368 | 0.18067 | 20.5323 | 0.85233 | 0.47291 | 6.8301 | 190.0594
07/16 21:37:30 |  | 1008.586 | 673.3368 | 1.4979 | 0.25 | 0.16089 | 0.14014 | 18.139 | 18.1588 | 18.1348 | 18.1781 | 18.1168 | 27.25 | 18.1455 | 20.5292 | 1.0053 | 28744.9182 | 0.25 | 0.14035 | 0.87105 | 0.16113 | 20.5292 | 0.85245 | 0.47291 | 6.8291 | 169.5528
07/16 21:45:00 | 26.975 | 1020.4536 | 681.3883 | 1.4976 | 0.25 | 0.16264 | 0.1417 | 18.1615 | 18.1799 | 18.1573 | 18.1977 | 18.1431 | 26.975 | 18.1679 | 20.5194 | 1.0075 | 28809.2276 | 0.25 | 0.14168 | 0.87125 | 0.16262 | 20.5194 | 0.84676 | 0.47291 | 6.8749 | 170.3649
07/16 22:00:00 | 26.7 | 829.5993 | 552.7453 | 1.5009 | 0.25 | 0.13255 | 0.11496 | 18.179 | 18.1966 | 18.1747 | 18.2135 | 18.1616 | 26.7 | 18.1851 | 20.5119 | 1.0096 | 28869.6559 | 0.25 | 0.11494 | 0.86724 | 0.13254 | 20.5119 | 0.84102 | 0.47291 | 6.9219 | 138.198
07/16 22:15:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.2038 | 18.2202 | 18.1995 | 18.2353 | 18.1881 | 26.7 | 18.2094 | 20.5013 | 1.0103 | 28888.3671 | 0 | 0 | 0 | 0 | 20.5013 | 0.84143 | 0.4729 | 0 | 0
07/16 22:30:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3127 | 18.3241 | 18.2999 | 18.3559 | 18.2685 | 26.7 | 18.3122 | 20.4565 | 1.0131 | 28967.7761 | 0 | 0 | 0 | 0 | 20.4565 | 0.84313 | 0.4729 | 0 | 0
07/16 22:45:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4206 | 18.4249 | 18.3998 | 18.4703 | 18.3526 | 26.7 | 18.4137 | 20.4124 | 1.0158 | 29046.509 | 0 | 0 | 0 | 0 | 20.4124 | 0.84474 | 0.4729 | 0 | 0
07/16 23:00:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.492 | 18.4909 | 18.4675 | 18.5397 | 18.4169 | 26.7 | 18.4814 | 20.3831 | 1.0177 | 29099.2854 | 0 | 0 | 0 | 0 | 20.3831 | 0.84577 | 0.4729 | 0 | 0
07/16 23:15:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5308 | 18.5264 | 18.5059 | 18.5724 | 18.4587 | 26.7 | 18.5188 | 20.3668 | 1.0187 | 29128.5217 | 0 | 0 | 0 | 0 | 20.3668 | 0.84633 | 0.4729 | 0 | 0
07/16 23:30:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5532 | 18.5472 | 18.5287 | 18.589 | 18.4856 | 26.7 | 18.5407 | 20.3573 | 1.0193 | 29145.6544 | 0 | 0 | 0 | 0 | 20.3573 | 0.84665 | 0.4729 | 0 | 0
07/16 23:45:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5708 | 18.564 | 18.5461 | 18.6022 | 18.5052 | 26.7 | 18.5576 | 20.35 | 1.0198 | 29158.888 | 0 | 0 | 0 | 0 | 20.35 | 0.8469 | 0.4729 | 0 | 0
07/16 24:00:00 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5869 | 18.5796 | 18.5617 | 18.6153 | 18.5212 | 26.7 | 18.5729 | 20.3434 | 1.0202 | 29170.8632 | 0 | 0 | 0 | 0 | 20.3434 | 0.84712 | 0.4729 | 0 | 0

## PerformanceCurves
|  |  | Name | VRFCoolCapFT | Name | VRFCoolCapFTBoundary | Name | VRFCoolCapFTHi
Rated Cooling Capacity [W] | 28594.11 |  | Coefficient1 Constant | 0.74718 | Coefficient1 Constant | 80.0017 | Coefficient1 Constant | 0.7827
Rated Cooling COP | 2.753 |  | Coefficient2 x | 0.0012296 | Coefficient2 x | -8.7793 | Coefficient2 x | 0.009836
Rated Cooling EIR | 0.36324 |  | Coefficient3 x**2 | 0.00083652 | Coefficient3 x**2 | 0.44988 | Coefficient3 x**2 | 0.00063346
Minimum Part Load Ratio | 0.25 |  | Coefficient4 y | 5.4235e-05 | Coefficient4 x**3 | -0.0080837 | Coefficient4 y | -0.0020247
TimeStep | 07/16 07:00:00 | 33 | Coefficient5 y**2 | -1.1173e-06 | Minimum Value of x | 15 | Coefficient5 y**2 | 1.4636e-06
Current TimeStep HAP Calculated COP | 0 |  | Coefficient6 x*y | -2.3573e-06 | Maximum Value of x | 23.9 | Coefficient6 x*y | -0.00022325
Current TimeStep HAP Calculated Cycling Ratio | 0 |  | Minimum Value of x | 15 | Minimum Curve Output | 10 | Minimum Value of x | 15
Current TimeStep HAP Calculated Runtime Fraction | 0 |  | Maximum Value of x | 23.9 | Maximum Curve Output | 22.2 | Maximum Value of x | 23.9
Current TimeStep HAP Calculated VRF Unit Power [W] | 0 |  | Minimum Value of y | -6.7 | Input Unit Type for X | Temperature | Minimum Value of y | 16.8
Outdoor Temperature [C] | 28.3 |  | Maximum Value of y | 22.2 | Output Unit Type | Temperature | Maximum Value of y | 43.3
Average Indoor Wetbulb [C] | 19.1188 |  | Minimum Curve Output | 0.95 |  |  | Minimum Curve Output | 0.837
VRF CoolCapFTBoundary [C] | 20.1053 |  | Maximum Curve Output | 1.263 |  |  | Maximum Curve Output | 1.263
VRF CoolCapFT | 1.0254 |  | Input Unit Type for X | Temperature |  |  | Input Unit Type for X | Temperature
Current Condition Cooling Capacity [W] | 29319.8036 |  | Input Unit Type for Y | Temperature |  |  | Input Unit Type for Y | Temperature
Current TimeStep Cooling Load [W] | 0 |  | Output Unit Type | Dimensionless |  |  | Output Unit Type | Dimensionless
Current TimeStep Part Load Ratio | 0.25
Heat Pump Cycling Ratio | 0
VRF Part Load Fraction | 0.85 |  | Name | VRFCoolEIRFT | Name | VRFCoolEIRFTBoundary | Name | VRFCoolEIRFTHi
VRF Run Time Fraction | 0 |  | Coefficient1 Constant | -0.57614 | Coefficient1 Constant | 80.0017 | Coefficient1 Constant | -1.4395
VRF EIRFTBoundary [C] | 20.1053 |  | Coefficient2 x | 0.12627 | Coefficient2 x | -8.7793 | Coefficient2 x | 0.16199
VRF EIRFT | 0.88834 |  | Coefficient3 x**2 | -0.0031562 | Coefficient3 x**2 | 0.44988 | Coefficient3 x**2 | -0.0034912
VRF EIRFPLR | 0.47291 |  | Coefficient4 y | 0.002479 | Coefficient4 x**3 | -0.0080837 | Coefficient4 y | 0.026944
Current TimeStep EIR | 0.1526 |  | Coefficient5 y**2 | 3.704e-07 | Minimum Value of x | 15 | Coefficient5 y**2 | 0.00013462
Current TimeStep COP | 6.5532 |  | Coefficient6 x*y | -4.3607e-05 | Maximum Value of x | 23.9 | Coefficient6 x*y | -0.00067149
Current TimeStep VRF Electric Power | 0 |  | Minimum Value of x | 15 | Minimum Curve Output | 10 | Minimum Value of x | 15
|  |  | Maximum Value of x | 23.9 | Maximum Curve Output | 22.2 | Maximum Value of x | 23.9
|  |  | Minimum Value of y | -6.7 | Input Unit Type for X | Temperature | Minimum Value of y | 16.8
|  |  | Maximum Value of y | 22.2 | Output Unit Type | Temperature | Maximum Value of y | 43.3
|  |  | Minimum Curve Output | 0.5996 |  |  | Minimum Curve Output | 0.6526
|  |  | Maximum Curve Output | 0.7252 |  |  | Maximum Curve Output | 1.2442
|  |  | Input Unit Type for X | Temperature |  |  | Input Unit Type for X | Temperature
|  |  | Input Unit Type for Y | Temperature |  |  | Input Unit Type for Y | Temperature
|  |  | Output Unit Type | Dimensionless |  |  | Output Unit Type | Dimensionless
|  |  | Name | CoolingEIRLowPLR | Name | CoolingEIRHiPLR | Name | CoolingCombRatio | Name | VRFCPLFFPLR
|  |  | Coefficient1 Constant | 0.45412 | Coefficient1 Constant | 1 | Coefficient1 Constant | 0.57659 | Coefficient1 Constant | 0.85
|  |  | Coefficient2 x | -0.17297 | Coefficient2 x | 0 | Coefficient2 x | 0.63494 | Coefficient2 x | 0.15
|  |  | Coefficient3 x**2 | 1.0829 | Coefficient3 x**2 | 0 | Coefficient3 x**2 | -0.30761 | Coefficient3 x**2 | 0
|  |  | Coefficient4 x**3 | -0.36185 | Coefficient4 x**3 | 0 | Coefficient4 x**3 | 0.096075 | Minimum Value of x | 0
|  |  | Minimum Value of x | 0.25 | Minimum Value of x | 1 | Minimum Value of x | 1 | Maximum Value of x | 1
|  |  | Maximum Value of x | 1 | Maximum Value of x | 1.5 | Maximum Value of x | 1.5 | Minimum Curve Output | 0.85
|  |  | Minimum Curve Output | 0.4729 | Minimum Curve Output | 1 | Minimum Curve Output | 1 | Maximum Curve Output | 1
|  |  | Maximum Curve Output | 1 | Maximum Curve Output | 1 | Maximum Curve Output | 1.1611 | Input Unit Type for X | Dimensionless
|  |  | Input Unit Type for X | Dimensionless | Input Unit Type for X | Dimensionless | Input Unit Type for X | Dimensionless | Output Unit Type | Dimensionless
|  |  | Output Unit Type | Dimensionless | Output Unit Type | Dimensionless | Output Unit Type | Dimensionless